## MVCP_map
Module | Element | Description | Modbus reg | Value type (1-BIT, 2-INT, 3-FLOAT) | R/W | min | max | Dimention | scale | Default Value | ValueList
MOTOR DATA | I(A) | The current of the motor in each of the three phases | 65 | 3 | R |  |  | A | 1 | 2.2
MOTOR DATA | I(%) | Operating current in each of the three phases as a percentage of motor FLA | 66 | 2 | W |  |  | % |  | 70
MOTOR DATA | VOLT | The voltage in each of the three phases | 67 | 3 | R |  |  | V |  | 1500
MOTOR DATA | FREQ | The line frequency | 68 | 2 | R |  |  | Hz |  | 50
MOTOR DATA | COSP | The motor power factor | 69 | 3 | R |  |  |  |  | 1
MOTOR DATA | Deg | Displays the angle (in degrees) between the voltage and the current | 70 | 2 | R |  |  | deg. |  | 0
MOTOR DATA | PW | Displays motor power | 71 | 3 | W |  |  | KW |  | 0
MOTOR DATA | Q | Displays motor reactive power | 72 | 3 | W |  |  | KVAR |  | 0
MAIN&PROTECT | RATED LINE VOLTAGE | HRVS-DN-PowerStart's rate voltage | 129 | 2 | W | 2300 | 15000 | V |  | 3300
MAIN&PROTECT | STARTER FLC | HRVS-DN-PowerStart's FLC (Full Load Current) | 130 | 2 | W | 20 | 1800 | A |  | 150
MAIN&PROTECT | MOTOR FLA | Sets motor's FLA(Full load Ampere) | 131 | 2 | W | 0 | 1800 | A |  | 150
MAIN&PROTECT | RATED MOTOR POWER | Sets motor rated power as indicated on its name plate | 132 | 2 | W | 50 | 40000 | KW |  | 1000
MAIN&PROTECT | SERVICE FACTOR | Sets motor rated service factor | 133 | 2 | W | 100 | 130 | % |  | 100
MAIN&PROTECT | UNDERCURRENT TRIP | Sets UNDER CURRENT TRIP protection. | 134 | 2 | W | 20 | 90 | % |  | 0
MAIN&PROTECT | UNDERCURRENT DELAY | Sets the time delay for UNDER CURRENT TRIP protection. | 135 | 3 | W | 0.2 | 40 | sec. |  | 1
MAIN&PROTECT | O/C SHEAR PIN | Sets OVER CURRENT SHEAR PIN protection | 136 | 3 | W | 0 | 5 | sec. |  | 0.1
MAIN&PROTECT | O/C DELAY | Sets O/C SHEAR PIN DELAY time. | 137 | 3 | W | 0 | 5 | sec. |  | 0.1
MAIN&PROTECT | OVERLOAD CLASS | Sets OVERLOAD CLASS characteristics | 138 | 5 | W |  |  |  |  | 2 | IEC CLASS 5,IEC CLASS 10,IEC CLASS 15,IEC CLASS 20,IEC CLASS 25,IEC CLASS 30,NEMA CLASS 5,NEMA CLASS 10,NEMA CLASS 15,NEMA CLASS 20,NEMA CLASS 25,NEMA CLASS 30
MAIN&PROTECT | OVERLOAD PROTECT ENABLE WHILE RUN | The overload protection can be set to protect the motor as set in the OVERLOAD PROTECT parameter | 139 | 5 | W |  |  |  |  | 2.2 | DISABLE, ENABLE WHILE RUN, ENABLE
MAIN&PROTECT | UNBALANCE TRIP | Sets UNBALANCE TRIP level | 140 | 2 | W | 10 | 100 | % |  | 20
MAIN&PROTECT | UNBALANCE DELAY | Sets UNBALANCE TRIP DELAY | 141.0 | 2 | W | 200 | 60000 | msec. |  | 1000
MAIN&PROTECT | GND FAULT TRIP | Sets GND FAULT TRIP level. | 141.1 | 2 | W | 10 | 100 | % |  | 20
MAIN&PROTECT | GND FAULT DELAY | Sets GND FAULT TRIP DELAY | 141.2 | 2 | W | 200 | 60000 | msec. |  | 5000
MAIN&PROTECT | UNDERVOLTAGE TRIP | Sets UNDER VOLTAGE TRIP level | 38.0 | 2 | W | 50 | 90 | % |  | 70
MAIN&PROTECT | UNDERVOLTAGE DELAY | Sets UNDERVOLT TRIP DELAY. | 145 | 3 | W | 0.2 | 10 | sec. |  | 5
MAIN&PROTECT | FREQUENCY TRIP | Sets the FREQUENCY TRIP. | 146 | 5 | W |  |  |  |  | 2 | DISABLE,ENABLE
MAIN&PROTECT | S.SCR OR WR.CON | Sets the S.SCR OR WR.CON trip. | 147 | 5 | W |  |  |  |  | 2 | DISABLE,ENABLE
MAIN&PROTECT | PHASE LOSS TRIP | Sets the PHASE LOSS TRIP | 148 | 5 | W |  |  |  |  | 1 | DISABLE,ENABLE
MAIN&PROTECT | VOLTAGE PLL TRIP | Sets the VOLTAGE PLL TRIP | 149 | 5 | W |  |  |  |  | 1 | DISABLE,ENABLE
START PARAMETERS | SOFT START CURVE | Sets HRVS-DN-PowerStart SOFT START CURVE | 195 | 5 | W | 0 | 5 |  |  | 1 | 0 (BASIC), 1 (STANDARD ), 2 !!, 3 !!, 4 !!, 5 (TORQUE)
START PARAMETERS | PULSE LEVEL | Sets PULSE LEVEL % OF FLA | 196 | 2 | W | 70 | 700 | % |  | 70
START PARAMETERS | PULSE TIME | Sets PULSE START TIME. | 197 | 3 | W | 0.0 | 0.64 | sec. |  | 0.1
START PARAMETERS | INITIAL VOLTAGE | Sets motor INITIAL STARTING VOLTAGE. | 198 | 2 | W | 10 | 50 | % |  | 10
STOP PARAMETERS | SOFT STOP CURVE | Sets SOFT STOP CURVE. | 260 | 5 | W | 0 | 4 |  |  | 1 | (BASIC), 1 (STANDARD ), 2 !!, 3 !!, 4 !!, 5 (TOR
STOP PARAMETERS | DECELERATION TIME | Sets DECELERATION TIME of the motor | 261 | 3 | W | 0 | 90 | sec. |  | 0.1
STOP PARAMETERS | FINAL TORQUE | Sets FINAL TORQUE during soft stop. | 262 | 2 | W | 0 | 10 | min. |  | 0.1
STOP PARAMETERS | COAST DOWN DELAY | Sets an Off delay timer that prevents the HRVS-DN-PowerStart to start before the COAST DOWN DELAY time has elapsed. | 263 | 2 | W | 10 | 3600 | sec. |  | 0
FAULT PARAMETERS | UV & PL AUTO RESET | Sets UNDERVOLTAGE and PHASE LOSS AUTO RESET. | 325 | 5 | W |  |  |  |  | 1 | NO,YES
FAULT PARAMETERS | BYPASS OPEN TRIP | Sets BYPASS OPEN TRIP protection | 326 | 5 | W |  |  |  |  | 2 | DISABLE,ENABLE
FAULT PARAMETERS | TRIP AFTER BYPASS | Sets TRIP AFTER BYPASS trip. | 327 | 5 | W |  |  |  |  | 2 | DISABLE,ENABLE
FAULT PARAMETERS | BYPASS AUTO RESET | Sets BYPASS AUTO RESET | 328 | 5 | W |  |  |  |  | 2 | NO,YES